pH Test for Feed Water

Apparatus

- Stoppered sample bottle

- Two 50ml Nessler cylinders

- Nessleriser

- Graduated glass dropper and bottle

- NLF Nessleriser disc pH 8.0-9.6

Reagents

- Thymol blue indicator

- Distilled water

Procedure

- Thoroughly rinse the sample bottle with the water to be tested. Completely fill and stopper immediately. Allow any suspended matter to settle but do not filter.

- Arrange the two Nessler cylinders side by side

- Add 0.2ml of thymol blue indicator solution from a graduated glass dropper into the right hand 50ml Nessleriser.

- Add 50ml of sample to the right hand Nessler cylinder.

- Add 50ml of sample to the other Nessler cylinder. This is the blank.

- Place the sample cylinder in the right hand compartment of the Nessleriser and the blank cylinder in the left hand compartment.

- Place NLF disc in Nessleriser and match the colours in the two windows using a constant light source.

- Read the pH value in the right hand window.