‘P’ Alkalinity Test/Phenolpthalein Alkalinity Test for Boiler Water

Apparatus

- Free standing plastic bottle and 25ml automatic burette

- 250ml porcelain dish

- 100ml graduated measuring cylinder

- Stirring rod

Reagents

- Sulphuric acid 0.2N

- Phenolpthalein indicator solution, 1%

Procedure

- Rinse the measuring cylinder with the water to be tested.

- Measure 100ml of the sample into the porcelain dish.

- Add ten drops of phenolphthalein indicator. If the sample is alkaline, a definite pink colour will appear.

- Using the burette, titrate with 0.02N sulphuric acid until the pink colour just disappears. Note the burette reading at this point.

- Retain the contents of the porcelain dish for the boiler water chloride test

Calculation

P alkalinity, as ppm of CaCO3 = ml of 0.02N sulphuric acid x 10