Phosphate Test for Boiler Water

Apparatus

- Two 25ml stoppered measuring cylinders

- Lovibond comparator

- Two comparator tubes

- Lovibond disc 3/60

- 3 inch filter funnel

- Whatman No 6 filter paper

Reagents

- Vanadomolybdate solution

Procedure

- Filter the sample through a Whatman No 6 paper or equivalent into a clean container discarding the first 20ml of solution.

- Check that the temperature of the sample and reagents is between 20oC and 30oC.

- Arrange the two 25ml stoppered cylinders side by side.

- Into the left hand cylinder add 10ml of distilled water.

- Into the right hand cylinder add 10ml of the filtered boiler water.

- Add 10 ml of vanadomolybdate solution to each cylinder making a total of 20ml in each cylinder.

- Stopper the cylinders and mix the contents by inverting several times.

- Allow to stand for 3 minutes.

- Transfer 5ml of the solution in the left hand cylinder to a clean dry comparator tube and place in the left hand compartment of the comparator.

- Transfer 5ml of the solution in the right hand cylinder to a clean dry comparator tube and place in the right hand compartment of the comparator.

- Insert comparator disc 3/60 in the comparator and rotate until a colour mathc is obtained. The number appearing in the small window is a direct reading of the amount of phosphate as PO4 in ppm.