Chloride Test for Feed Water

Apparatus

- Microburette

- 100ml measuring cylinder

- 250ml porcelain dish

- Stirring rod

- Two dropper bottles

Reagents

- Potassium chromate solution, 2 or 5%

- Silver nitrate solution 0.02N

- Phenolpthalein indicator solution, 1%

- Sulphuric acid 0.02N

Procedure for blank determination

- Add 100ml of distilled water to the porcelain dish.

- Add ten drops of potassium chromate indicator solution; the sample will turn yellow.

- Add 0.02N silver nitrate solution by titrating, using the microburette, until the first colour change to brick red is noted.

- Record the ml of silver nitrate used.

Procedure for sample determination

- Add 100ml of the filtered sample water to a clean porcelain dish.

- Add ten drops of phenolphthalein solution; the sample will turn pink.

- Titrate with 0.02N sulphuric acid until the pink colour just disappears.

- Add ten drops of potassium chromate solution; the sample will turn yellow.

- Add 0.02N silver nitrate solution by titrating from the microburette until the first colour change to brick red is noted.

- Note the ml of silver nitrate used.

Calculation of results

S – B = Chloride as ppm CaCO3

where

S = ml of silver nitrate used to titrate the sample

B = ml of silver nitrate used to titrate the blank