Short Term Storage

Neglect of boilers during standing periods frequently leads to the onset of corrosion in the steam and water spaces from which serious attack may develop during subsequent working periods. Corrosion can start as soon as a boiler is emptied, and the attack will be especially severe if pools of water are left in the boiler. In all cases, the boiler should be dried out as soon as possible.

During short term idle periods, one of the following methods of protection, whichever is most convenient, should be used:

- Completely filling the boiler with alkaline water containing sufficient catalysed sodium sulphate to combine with the dissolved oxygen and leave an excess of 200 ppm Na2SO3; before sealing the boiler, the water should be raised to the boiling point to induce mixing by circulation and to complete the chemical reaction.

- Completely filling the boiler with alkaline water containing sufficient hydrazine to combine with the dissolved oxygen and leave an excess of hydrazine; for short periods of storage, up to three days, the hydrazine excess to be at least 25 ppm N2H4; before sealing the boiler, the water should be raised to the boiling point to induce mixing by circulation and to complete the chemical reaction.

When using the above methods the alkalinity should be raised to the recommended value by the addition of the appropriate chemical normally used. It is also necessary to check periodically the excess of sulphate or hydrazine in the boiler water and to restore any that has been oxidized. If the boiler is not being emptied then the sodium sulphate or hydrazine should be added a short time before steaming ceases. The treatment, in solution, should be directly injected into the boiler or added as a single shot at the feed tank.

When using these methods, precautions should be taken to prevent atmospheric condensation upon the fire side surfaces of the boiler, which would lead to severe external corrosion.

Wet storage methods are not advised in circumstances in which the water in the boiler could freeze during idle periods.