Calcium and Magnesium (Hardness Salts)

Source

- Carryover of sea water droplets from evaporator

- Leakage of sea water into condensate system

- Use of untreated fresh water as boiler make-up

- Use of water from lime-washed or cement coated tanks

Effects of Calcium

- Formation of calcium phosphate, calcium carbonate and calcium sulphate deposits in boiler.

- Loss of phosphate reserve in boiler.

- Loss of alkalinity and pH in boiler water.

- Corrosion of boiler surfaces due to high chloride ion concentration and possible formation of hydrochloric acid in the boiler.

Effects of Magnesium

- Formation of magnesium hydroxide deposits in boiler.

- Loss of alkalinity and pH in boiler water.

- In extreme cases loss of phosphate from boiler water with formation of magnesium phosphate deposits in boiler.

- Corrosion of boiler surfaces due to high chloride ion concentration and possible formation of hydrochloric acid.

Prevention

- Minimize carryover of sea water from evaporator.

- Stop leaks of sea water to condensate system.

- Do not use untreated fresh water as boiler make-up.

- Do not use water from lime-washed or cement-lined tanks.

- Maintain recommended level of alkalinity and phosphate in boiler water.