IRON

Source

- Corrosion of mild steel condensate return lines due to oxygen and carbon dioxide dissolved in the condensate producing low pH of condensate.

- Corrosion of mild steel in boiler feed system due to low pH and oxygen in feed.

- Erosion of metal from pipes and components containing steam and water mixtures at high or uncontrolled flow rates. E.g.

  - High pressure drain pipes

  - Steam trap drain lines

  - High pressure feed water heaters

    - Use of boiler feed water which has been stored in unlined tanks resulting in corrosion of the tank and high iron in feed water.

    - Attack on boiler due to

      - Acid conditions

      - High chlorides

      - Overheating of boiler metal due to deposits in the boiler tubes or water starvation in boiler

Effects

- Deposition of iron oxide on boiler tubes. As the thickness of these deposits builds up, overheating of the tubes will occur.

Prevention

- Control the condensate pH to between 8.8-9.3.

- Stop air leaks into condenser and condensate system.

- Control the feed water pH to between 8.8-9.3.

- Ensure the deaerator is operating efficiently by daily checks on residual oxygen content.

- Maintain recommended level of alkalinity in boiler.

- Do not exceed quoted level of chloride in boiler.

- Never fire boiler with low water levels.