DISSOLVED OXYGEN

Cold water contains between 8-10 mg/l of dissolved oxygen. The level of oxygen in water used in marine boilers should be zero.

Source

- Already in the water.

- Insufficient deaeration of feed water.

- Air leaks in condenser and condensate system.

- Inadequate feed of hydrazine to the deaerated feed water.

- General leaks.

Effects

- Attack on boiler metal resulting in pitting and deposition of iron oxide on the boiler tubes.

- Corrosion of condensate system to produce iron and copper in the condensate. Copper is attacked by ammonia in the presence of oxygen.

Prevention

- Ensure that the deaerator is working efficiently.

- Stop air leaks into condenser, condensate and boiler feed system.

- Ensure that correct level of hydrazine is being added to the deaerated feed water.