Deaeration

The two most aggressive gasses in distilled sea water are oxygen and carbon dioxide, and a combined attack on the mild steel by both is far more damaging than the sum of the damage caused by the two gases acting independently.

Cold water usually contains about 8-10 mg/l of dissolved oxygen, but as the temperature of the water approaches boiling point, its ability to dissolve oxygen decreases to approximately 1 mg/l.

The normal 1 mg/l level of dissolved oxygen in boiling water is harmful to boilers and in order to reduce the level to acceptable limits, it is usual to include a deaerator in the feed water system. Furthurmore, due to the thermal breakdown of bicarbonate in the evaporator, distilled water usually contains dissolved carbon dioxide and this too must be removed.